## GSHP Checklist
NYS Clean Heat Statewide Heat Pump Program
Standards and Quality Assurance
Ground Source Heat Pump Checklist
Updated: 9/1/2025
# | Category | Objective / Task Description | Criteria | Document Required / Verification Method | Responsible Party | Program Phase | Defect Category | Reference
D1 | Design Doc't. | Confirm the bore well/ ground loop design document was submitted and matches the project site (address, physical description) | Document Review | Bore well/ground loop design document | Participating Contractor | Design | Major
D2 | Design Doc't. | Confirm soil type and conductivity assumptions are listed in the bore well/ground loop design document. | Document Review | Bore well/ground loop design document | Participating Contractor | Design | Minor
D3 | Design Doc't. | Confirm the bore well/ ground loop design document shows the flow rate determination and min/max entering temperatures (n/a for DX systems) | Document Review | Bore well/ground loop design document | Participating Contractor | Design | Minor
D4 | Design Doc't. | Confirm the bore well/ ground loop design document shows the acceptable type and concentration of antifreeze (n/a for DX systems) | Document Review | Bore well/ground loop design document | Participating Contractor | Design | Minor
D5 | Design Doc't. | Confirm the bore well/ ground loop design document shows manifold design and location | Document Review | Bore well/ground loop design document | Participating Contractor | Design | Minor
D6 | Startup Checklist - Design Doc't. | Verify if a startup checklist was provided, that contained the following elements 1. Heat exchanger water flow test and test method 2. Water quality documentation 3. Water temperature differential, pressure, flow documentation 4. Antifreeze concentration and type documentation 5. Flushing purging procedure documentation 6. Ground heat exchanged leak test documentation and test method 7. Condensate drain function testing 8. Observed functional testing in heating and cooling modes 9. Air filter installation verification if applicable | Document Review | NYC ECC EN2/TR8 forms or equivalent / Startup Checklist | Participating Contractor | Commissioning | Major
DDX6 | Startup Checklist - Design Doc's (DX only) | Verify if a startup checklist was provided, that contained the following elements (DX systems): 1) Verification that the system was vacuumed down to 500 microns or less. 2) Document the refrigerant volume used to charge the system 3) Condensate drain function testing 4) Observed functional testing in heating and cooling modes 5) Air filter installation verification if applicable 6) Method of cathodic protection documented (induced current or magnesium anode) | Document Review | NYC ECC EN2/TR8 forms or equivalent / Startup Checklist | Participating Contractor | Commissioning | Major
C1 | Equipment | Verify installed equipment is as proposed on the invoice or application documentation, including quantity, make and model information. | Document Review | Field Observation or Photo Documentation | Participating Contractor | Construction | Major
C2 | Installation | Verify that safe access to the site and associated equipment has been provided | Situational Awareness | Site Observation | Participating Contractor | Construction | Critical
C3 | Installation | Verify site conditions are consistent with the submitted Load Sizing Analysis, and that the analysis used an ACCA approved Manual J software platform or received a program exception. | Visual Observation / Document Review | Design report referencing ACCA .Manual J, S, and D) or other approved heating and cooling calculation methodologies. Site observation. | Participating Contractor | Construction | Major | NYC DOB EN2: As Built Energy Analysis https://www.acca.org/standards/approved-software
C4 | Installation | If accessible - confirm manifold are consistent with design documentation | Document Review | Approved construction documents and photo documentation | Participating Contractor | Construction | Minor
C5 | Installation | Observe condensate and defrost lines where accessible for leaks. Confirm condensate/defrost lines terminate in either a domestic drain before a trap or external location. Defrost must not drain onto other heat pumps or where refreeze will occur on walking surfaces. Condensate must not drain onto an external stairway. Condensate and defrost drainage must flow freely. Confirm with the homeowner that there is no indication of condensate line leakage before the termination point. | Visual Observation / Photo Documentation / Customer Confirmation | Site Observation / Customer Confirmation | Design Professional / Participating Contractor | Construction | Major
C5B | Installation | Confirm condensate and defrost lines do not terminate in any of the following locations: Drain, waste, vent (DWV) lines after traps, directly against wood walls or structural components, within the line hide, onto a flat surface that has no drainage, or to other locations that would likely cause property damage or occupant danger. | Visual Observation / Photo Documentation / Customer Confirmation | Site Observation / Customer Confirmation | Design Professional / Participating Contractor | Construction | Minor | International Mechanical Code Chapter 11 - CODE: 307.2.1.1 Condensate discharge
C6 | Installation | Verify piping through wall or floor surfaces is properly sealed. | Document Review | Approved construction documents and photo documentation | Participating Contractor | Construction | Minor
C7 | Installation | Verify that exposed new or retrofitted ductwork is properly sealed and insulated if located outside the building's thermal envelope. | Visual Observation / Photo Documentation | Site Observation / NYC ECC EN2/TR8 forms or equivalent | Participating Contractor | Construction | Major | NYC 1RCNY 5000- 01
C8 | Installation | Confirm all exposed equipment appears to be properly secured; unit and associated piping and ductwork are secured in a manner to prevent damage. | Visual Observation / Photo Documentation | Site Observation | Participating Contractor | Construction | Major
C9 | Installation | Verify that electrical disconnect is installed in an accessible location for service. | Visual Observation / Photo Documentation | Site Observation | Participating Contractor | Construction | Major | As referred to in the 2017 NEC Article 440.14
C10 | Installation | In areas formerly heated, directly or indirectly, by a fossil fuel heating system, confirm that any plumbing outside the thermal envelope is adequately protected from freezing by insulation, heat, or both. | Visual Observation | Site Observation | Design Professional/Participating Contractor | Occupancy | Major
C11 | Installation | Verify all indoor contractor-installed refrigerant lines and/or loop field supply/return piping is properly insulated to manufactures specifications. To comply, no more than 2" of any accessible contractor-installed refrigerant line and/or loop field supply/return piping may be left un-insulated. | Visual Observation/Photo Documentation | Site Observation/Photo Documentation | Design Professional/Participating Contractor | Construction | Major
C12 | Installation | (applicable for Category 8 projects) Verify that the GSHP water-to-water heat pump is the only energy source supplying domestic hot water in the building. | Visual Observation/Photo Documentation | Site Observation/Customer Confirmation | Design Professional/Participating Contractor | Construction | Major
CDX1 | Installation | Verify cathodic protection on piping where applicable using either induced current or magnesium anode (DX Systems) | Visual Observation / Photo Documentation/ Document Review | Approved construction documents / Site Observation / Photo Documentation | Participating Contractor | Construction | Major
CDX2 | Installation | Verify all indoor and outdoor refrigerant line sets (liquid and vapor) are insulated. Any refrigerant line sets situated outdoors are also protected from UV. (DX systems) | Visual Observation / Photo Documentation | Site Observation / Photo Documentation | Participating Contractor | Construction | Major
CED1 | Equipment - Desuperheater / WWHP (optional) | Verify temperature and pressure relief valve and discharge tube are installed on the pre-fill or water tank as required and that the relief valve terminates within 6" of the floor. | Visual Observation / Photo Documentation | Site Observation | Participating Contractor | Construction | Major
CED2 | Equipment - Desuperheater / WWHP (optional) | Verify outdoor unit, indoor unit, tanks, heat exchangers, and pump connections (if applicable) are leak free. | Visual Observation / Photo Documentation / Document Review | Site Observation | Participating Contractor | Construction | Minor
O1 | Operation | Confirm that the system owner's manual and maintenance instructions are available on site. The maintenance log must detail loop location description, loop piping material, required maintenance schedule on loop field and heat pump. (n/a for DX systems) | Visual Observation / Photo Documentation / Document Review | Site Observation / Startup Checklist | Participating Contractor | Construction | Minor
O2 | Operation | Confirm customer/ operator has been provided with training on operation of system. | Document Review | Site Observation / Customer Confirmation / Startup Checklist | Participating Contractor | Occupancy | Minor
O3 | Operation | Confirm the distribution system is capable of providing sufficient comfort to all spaces conditioned by the heat pump unit(s). | Visual Observation/Customer Confirmation | Site Observation/Customer Confirmation | Design Professional/Participating Contractor | Occupancy | Major
ODX1 | Operation | Confirm that the system owner's manual and system specifications are available on site. These should the loop field refrigerant content, type, and volume. (DX Systems) | Visual Observation / Photo Documentation / Document Review | Site Observation / Startup Checklist | Participating Contractor | Construction | Minor