## HPWH Checklist
NYS Clean Heat Statewide Heat Pump Program
Standards and Quality Assurance
Heat Pump Water Heater Checklist
2025-09-01
# | Category | Objective / Task Description | Criteria | Document Required / Verification Method | Responsible Party | Program Phase | Defect Category | Reference
A1
C1 | Equipment | Verify installed equipment is as proposed on the invoice or application documentation, including quantity, make and model information. | Visual Observation / Photo Documentation | Photo Documentation | Participating Contractor | Construction | Major
C2 | Installation | Observe condensate line where accessible for leaks. Confirm condensate lines terminate in either a domestic drain or external location. External locations must not terminate onto another heat pump unit or onto a walking surface that could cause slips if condensate freezes. Confirm with the homeowner that there is no indication of condensate line leakage. | Visual Observation / Photo Documentation / Customer Confirmation | Site Observation / Customer Confirmation | Design Professional / Participating Contractor | Construction | Major
C3 | (Intentionally Blank)
C4 | Installation | Verify temperature and pressure relief valve are installed and that the relief valve terminates within 6" of the floor. | Visual Observation / Photo Documentation | Site Observation | Participating Contractor | Construction | Minor
C5 | Installation | Verify that safe access to the site and associated equipment has been provided | Situational Awareness | Site Observation | Participating Contractor | Construction | Critical
C6 | Installation | Verify unit has sufficient makeup air for sustained efficient operation. A ducted unit, split unit, or a unit with at least 700 cubic feet of connected space complies. | Visual Observation / Photo Documentation | Site Observation | Participating Contractor | Construction | Major
C7 | Installation | Verify that the first 6 feet of hot-water line from the unit has been insulated or is a non-conductive piping material (e.g. PEX). Verify that any exposed hot and cold water lines are not in direct contact, regardless of material. | Visual Observation / Photo Documentation | Site Observation / NYC ECC EN2/TR8 forms or equivalent | Participating Contractor | Construction | Minor | NYC 1RCNY 5000-01
C8 | (Intentionally Blank)
C9 | Installation | Verify all exposed equipment and pipe supports appear to be properly secured | Visual Observation / Photo Documentation | Site Observation | Participating Contractor | Construction | Major
C10 | Installation | Verify water heater connections and system are leak free | Functional test | Site Observation | Participating Contractor | Construction | Major
C11 | Installation | For ducted indoor units, verify air outlet of ducted HPWH exhausts to the outdoors, and that duct size is appropriate | Visual Observation / Photo Documentation | Site Observation | Participating Contractor | Construction | Major
C12 | Installation | For ducted indoor units, verify booster fan installed on outlet duct if required | Visual Observation / Photo Documentation | Site Observation | Participating Contractor | Construction | Major
C13 | Installation | Verify that electrical disconnect is installed in an accessible location for service. If located outside of view from the unit, the disconnect is lockable. | Visual Observation / Photo Documentation | Site Observation | Participating Contractor | Construction | Major
C14 | (Intentionally Blank)
C15 | Installation | Observe functional testing of equipment. | Functional Test | Site Observation | Participating Contractor | Construction | Major
C16 | Installation | Provide sufficient clearance to allow for service and maintenance as per manufacturer's specifications. | Visual Observation / Photo Documentation | Site Observation | Participating Contractor | Construction | Major
S1 | Installation - Split (Optional) | For split / outdoor units, verify heat trace has been installed on water lines to the outdoor unit if applicable | Visual Observation / Photo Documentation | Site Observation | Participating Contractor | Construction | Major
S2 | Installation - Split (Optional) | For split units, sample for refrigerant leaks at exposed field connections | Functional Test | Refrigerant detector | Participating Contractor | Construction | Critical
S3 | Installation - Split (Optional) | For split/outdoor units, verify outdoor unit is installed with sufficient clearances per manufacturer's requirements. | Visual Observation / Photo Documentation | Site Observation | Participating Contractor | Construction | Major
S4 | Installation - Split (Optional) | Observe that the outdoor unit is away from or protected from increased sources of water/ice/snow from above (i.e. more than normal precipitation, e.g. beneath drip edge, beneath snow-slide, beneath another heat pump, etc.). The presence of gutters does provide sufficient protection for asphalt roofs. The presence of gutters does not provide sufficient protection for all other pitched roof types. | Visual Observation / Photo Documentation | Site Observation / Photo Documentation | Participating Contractor | Construction | Major
S5 | Installation - Split (Optional) | Verify that units are above snow depth level according to ACCA Weather Station data. | Visual Observation / Photo Documentation | Site Observation / Photo Documentation | Participating Contractor | Construction | Major
S6 | Installation - Split (Optional) | For split / outdoor units, verify outdoor unit is installed level. | Visual Observation / Photo Documentation | Site Observation | Participating Contractor | Construction | Major
S7 | Installation - Split (Optional) | If unit is connected to the building's framing (e.g. wall mounted, or on a connected deck), vibration dampeners are installed. | Visual Observation / Photo Documentation | Site Observation | Participating Contractor | Construction | Minor
S8 | Installation - Split (Optional) | For split / outdoor units, verify height difference between outdoor unit and storage tank are within specified limits | Visual observation / Document Review | Site Observation | Participating Contractor | Construction | Major
S9 | Installation - Split (Optional) | Confirm the outdoor unit’s defrost drainage does not terminate onto other heat pumps or where refreeze will occur on walking surfaces. | Visual Observation / Photo Documentation / Customer Confirmation | Site Observation / Customer Confirmation | Design Professional / Participating Contractor | Construction | Major
O1 | Operation | Verify approval of work in accordance with applicable codes | Document Review | Cert. of Completion / CoO / Letter of Attestation | Participating Contractor | Occupancy | Critical
O2 | Operation | Verify Manufacturer's Warranty has been provided to owner | Document Review | Manufacturers Warranty | Participating Contractor | Occupancy | Minor
O3 | Operation | Confirm customer/ operator has been provided with training on operation of system. | Document Review | Site Observation / Customer Confirmation | Participating Contractor | Occupancy | Major
O4 | Installation | Confirm that the system owners manual and maintenance instructions are available on site | Document Review | Approved construction documents | Participating Contractor | Design | Minor