## AWHP Checklist
NYS Clean Heat Con Edison Heat Pump Program
Standards and Quality Assurance
Air to Water Heat Pump Checklist
Updated: 5/17/2024
# | Applicable System Type | Objective / Task Description
DMH1 | Hydro-Split Monobloc | Verify if a startup checklist was provided, that contained the following elements (n/a for DX split systems) 1. Antifreeze type and concentration documentation. 2. Burst temperature documentation. Burst temperature must be at least 10°F lower than the 99% outdoor air heating design temperature. 3. Load side leak test and test method documentation (downstream piping). 4. Source side leak test and test method documentation (upstream piping). 4. Water source, water quality testing, water treatement method documentation. 5. Water to water heat exchanger temperature and pressure differential test documentation (only applicable if W2W HEX exists). 6. Flushing procedure documentation. 7. Purging procedure documentation. 8. Functional testing with space setpoint temperature, outdoor air temperature, system flow rate, leaving water temperature documented in both heating and cooling mode as conditions allow.
DDX1 | DX split | Verify if a startup checklist was provided, that contained the following elements Refrigerant Loop Side Checks 1. Documentation that the system was vacuumed down to 500 microns or less. 2. Documentation of the refrigerant volume used to charge the system. 3. Documentation of the Actual and Target Superheat (°F) or the Actual and Target Subcooling (°F). 4. Documentation of condensate drain function testing 5. Documentation of functional testing in heating and cooling modes 6. Air filter installation verification if applicable Hydronic Side Checks 1. Load side leak test and test method documentation (downstream piping). 2. Water source, water quality testing, water treatement method documentation. 3. Flushing procedure documentation. 4. Purging procedure documentation. 5. Functional testing with space setpoint temperature, outdoor air temperature, system flow rate, leaving water temperature documented in both heating and cooling mode as conditions allow.
D2 | All | Verify design schematic (engineering drawing or output from manufacter design tools) and sequence of operations documentation have been provided.
D3 | All | Verify the Sizing and Design Calculator is complete and is consistent with site conditions. Verify the total AWHP equipment heating load ratio and room by room heating load ratios are within 100 to 120%.
C1 | All | Verify installed equipment is as proposed on application, quantity, make and model
C3 | All | Verify outdoor unit, indoor unit, tanks, heat exchangers, and pump connections (if applicable) are leak free.
C5 | All | Verify site conditions are consistent with Load Sizing Analysis or a revised energy analysis has been completed. Review of ACCA (Manual J, S, and D) or other approved heating and cooling calculation methodologies, with observed site conditions
C6 | All | Verify that the first 6' of hydronic heating circulation piping from the indoor unit/storage tank to the heat emitters are insulated. Verify that any exposed hot water lines are not in direct contact, regardless of material.
C7 | All | Verify that the hydronic cooling lines from the indoor unit/storage tank to terminal units are insulated and vapor sealed. Verify that any exposed cold water lines are not in direct contact, regardless of material.
C8 | Hydro-Split Monobloc | Verify that the outdoor hydronic piping is insulated with freeze protection.
C11 | All | Verify temperature and pressure relief valve are installed on any pressure tanks and that the relief valve terminates within 6" of the floor.
C13 | All | Verify outdoor unit is installed with sufficient clearances per manufacturer's requirements.
C15B | All | Verify that units are above snow depth level according to ACCA Weather Station data as provided by the NYS Clean Heat program
C16 | All | Verify outdoor unit is installed level.
C17 | All | Observe functional testing of equipment in either cooling or heating mode as conducted by contractor or operator, if conditions allow.
C18 | All | Verify that electrical disconnect is installed in an accessible location for service.
CDX1 | DX split | Sample for refrigerant leaks at exposed field connections without moving insulation around linesets.
CDX2 | DX split | Verify all accessible refrigerant line (indoor and outdoor) set is insulated. Verify that all outdoor refrigerant line set is protected from UV. To comply, no more than 12" of any accessible refrigerant line may be left un-insulated/protected from UV at the outdoor unit connection.
DE2 | All | Confirm the contractor-completed Decommissioning Guidance Checklist matches conditions on site.
DE3 | All | Verify fossil fuel space heating appliance has been removed from site or fuel lines to appliance have been cut and capped.
DE4 | All | (if applicable) Verify fossil fuel domestic hot water appliance has been removed from site or fuel lines to appliance have been cut and capped