## Residential ASHP-GSHP Checklist
NYS Clean Heat
Con Edison Heat Pump Program
Residential Sector (ASHP & GSHP)
Standards and Quality Assurance
Updated: 10/1/24
Effective: 10/25/24
Protocol for Immediate Safety Concerns • The inspector should notify the customer concerning any Immediate Safety Concern finding and emphasize that these conditions must be urgently addressed. • The Inspector should then notify their management, Con Edison, and the Participating Contractor. • Con Edison requires Participating Contractors to address such concerns immediately, and at all times as soon as reasonably practicable, with an expectation of within 24-hours of notice if the facts and circumstances allow.
| # | Objective / Task Description
All Projects | C1 | Verify installed equipment is as proposed on application, quantity, make and model
| C1A | Minor typos on application for model or serial numbers that do not impact sizing or equipment eligibility
| C5 | Verify site conditions are consistent with Load Sizing Analysis or a revised energy analysis has been completed. Review of ACCA (Manual J, S, and D) or other approved heating and cooling calculation methodologies, with observed site conditions
| C15B | Verify that units are above snow depth level according to ACCA Weather Station data as provided by the NYS Clean Heat program. Only applicable to ASHP applications
| C17 | Observe functional testing of equipment in either cooling or heating mode as conducted by contractor or operator, if conditions allow.
| C18 | Verify that electrical disconnect is installed in an accessible location for service.
Integrated Controls Only | IC1 | Confirm integrated control system has been installed and is operational. Contractor documentation must specify the controls settings on-site, referencing set points and control type. Only applicable to ASHP applications.
| IC2 | Confirm integrated control system matches that of the application and is listed on the Qualified Product List. Only applicable to ASHP applications
Decommissioning Only | DE2 | Confirm the contractor-completed Decommissioning Checklist matches conditions on site.
| DE2A | Conditions on site have fully met requirements in Decommissioning Checklist but the checklist itself was filled out incorrectly.
Decommissioning Safety | SF1 | NATURAL GAS ONLY: Visually verify that visible fuel line(s) to the decommissioned appliance have been disconnected, removed, and capped with a press fitting or a threaded fitting using thread sealant. Visually verify that the cap appears to be tight and secure. Verify that no odor or sound of leaking gas is detected by smelling and listening.
| SF2 | OIL OR PROPANE ONLY: Visually verify oil fuel lines to decommissioned appliance(s) have been disconnected, removed and capped using a threaded fitting and that the cap appears to be tight and secure. Visually verify that oil or propane does not appear to be leaking.
| SF3 | Verify disconnection of power supply to decommissioned space heating appliance. Visually verify that no exposed wires can be seen.
| SF4 | Visually verify that a working smoke and CO detector is present. Look for a blinking light on the detector and test the device by pressing the button according to the device's instructions if it can be reached.
Venting | V1 | Visually verify that rigid metal caps with threaded fasteners have been used to seal flue vents previously used by the decommissioned appliance(s)
| V2 | For commonly vented systems with an operational DHW or combustion appliance, confirm that the remaining is free of visible defects, pitched upward toward the chimney, and supported.